CONTENTS

FOREWORD

SUMMARY

1	INTRODUCTION

1.1	Circumstances Leading up to this Investigation

1.2	Objectives

1.3	Methodology

1.4	Statistical Analysis

2	MOX FUEL MANUFACTURE AT SELLAFIELD

2.1	History of MOX Fuel

2.2	MOX Fuel Production Process

2.2.1	Fuel Pellet Production

    - Fuel Rod Production

    - Quality Control/Quality Assurance Procedures

3	INVESTIGATION FINDINGS

3.1	Extent of Falsification

3.2	Who was Involved

3.3	Why Falsification Happened

3.4	Adequacy of BNFL’s own Investigation

3.5	Management Shortcomings in Control and Supervision

4	ASSESSMENT OF THE SAFETY OF MDF FUEL IN USE

4.1	Factors Affecting Fuel Safety in Use

4.2	NII's Views

5	REQUIREMENTS FOR THE RESTART OF MDF

5.1	Plant and Equipment

5.2	Process Workers

5.3	Supervisors

5.4	Plant Management

5.5	Site Management

5.6	BNFL Corporate Management

6	CONCLUSIONS

Appendix 1	Summary of key Events

Appendix 2	Important Fuel Quality Characteristics

Appendix 3	Fuel Rod Failure Mechanisms

TABLE 1	MOX Fuel Pellet Lot Numbers with Falsified Data

TABLE 2	key MOX Fuel Pellet Quality Characteristics

TABLE 3	key MOX Fuel Rod Quality Characteristics

18 February, 2000

An Investigation into the Falsification of Pellet Diameter Data in the MOX

Demonstration Facility at the BNFL Sellafield Site

and the Effect of this on the Safety of MOX Fuel inUse

SUMMARY

The MOX Demonstration Facility (MDF) at BNFL's Sellafield site manufactures MOX (mixed oxides of plutonium and uranium) fuel pellets and assembles these using various customer supplied components to make complete fuel assemblies for use in nuclear power reactors. Each fuel pellet produced passes through a fully automated laser micrometer which checks and records the pellet's diameter at three points along its length, giving a 100% automatic check on all pellets used in a fuel rod. Any undersized or oversized pellets are automatically rejected. Those which fall within the specified diametral tolerance pass onto the next stage where each undergoes further visual checks. As a confirmatory check on diameter and in accordance with the 1% Acceptable Quality Level (AQL) criterion set out in BS 6001, a sample of 200 pellets (approximately 5%) which have passed through both these stages is measured for a second time. This quality check is done using a similar micrometer, but the sample pellets are presented to the micrometer by process workers who type each measured diameter, e.g. 8.195mm, into a computer spreadsheet.

On 20 August 1999 a member of MDF's Quality Control Team identified similarities between the secondary pellet diameter data for successive Lots.    After further investigations, on 10 September 1999 BNFL reported to NII that some of these secondary pellet diameter checks on the fuel manufactured for a Japanese customer appeared to have been falsified by copying some data between spreadsheets.

The Health and Safety Executive's Nuclear Installations Inspectorate (NII) promptly launched an investigation to establish both the extent of the falsification and the causes of the event. NII concluded that data had indeed been falsified but that this would not affect the safety performance of the fuel, given the automated primary diameter check on 100% of the pellets used in each fuel rod.

NII believes the failure to properly carry out the agreed manual checks of the pellet diameter to be a contractual issue between BNFL and its customer.    However, because it also represents a deliberate breach of operating procedures the Inspectorate launched an investigation which centred upon:

i)	understanding just what had occurred in MDF and why;

ii)	whether the fuel involved will be safe in use; and

iii)	what needs to be done to prevent any recurrence.

NII's investigation into possible reasons for the falsification identified that although various individuals were at fault, a systematic failure allowed it to happen.    In a plant with the proper safety culture, the events described in this report could not have happened.

NII commissioned an independent analysis by HSE's statisticians of the extent of the falsification. The results of this and further manual checks of data by NII showed that the initial investigation by BNFL, carried out under severe time pressures was too narrow: there had been a tendency to rush to early conclusions which understated the extent of the problem by assuming that the falsification was largely confined to one shift. Nevertheless BNFL agreed to carry out further, more detailed investigations and, following discussions with NII, has taken steps to address the contributory factors to this incident which the Company and the Inspectorate have identified.

NII is satisfied that in spite of the falsification of the quality assurance related data, the totality of the fuel manufacturing quality checks are such that the MOX fuel produced for Japan will be safe in use. With regard to MDF, the plant is shut down and will not be allowed to restart until NII is satisfied that the recommendations outlined in this report have been implemented to ensure, inter alia, that the deficiencies found in the quality checking process have been rectified, the management of the plant has been improved and plant operators have been either replaced or retrained to bring the safety culture in the plant up to the standard NII requires for a nuclear installation.